## ReadRegisters
Reading registers (Function code $04)
All values are written in big endian byte order in Modbus messages
Register addresses are not Modbus register names but the actual address values that must be written in messages
Parameter | Register Type | F. Code | Address | Words | Unit | Type | Enumeration or other details
Charger modbus (socket 0.0.0.0:502)
Real time values
Connector 1 • Connnector status | Input Register | 4 | 0 | 1 |  | Int16 | ConnectorStatus
Connector 1 • Measured vehicle number of phases | Input Register | 4 | 1 | 1 |  | Int16 | NumberOfPhases
Connector 1 • EV max phase current | Input Register | 4 | 2 | 2 | A | Float32
Connector 1 • Target current from power mgm or modbus | Input Register | 4 | 4 | 2 | A | Float32
Connector 1 • Frequency | Input Register | 4 | 6 | 2 | Hz | Float32
Connector 1 • L-N voltage (L1) | Input Register | 4 | 8 | 2 | V | Float32
Connector 1 • L-N voltage (L2) | Input Register | 4 | 10 | 2 | V | Float32
Connector 1 • L-N voltage (L3) | Input Register | 4 | 12 | 2 | V | Float32
Connector 1 • Curent (L1) | Input Register | 4 | 14 | 2 | A | Float32
Connector 1 • Curent (L2) | Input Register | 4 | 16 | 2 | A | Float32
Connector 1 • Curent (L3) | Input Register | 4 | 18 | 2 | A | Float32
Connector 1 • Active power (L1) | Input Register | 4 | 20 | 2 | kW | Float32
Connector 1 • Active power (L2) | Input Register | 4 | 22 | 2 | kW | Float32
Connector 1 • Active power (L3) | Input Register | 4 | 24 | 2 | kW | Float32
Connector 1 • Active power (total) | Input Register | 4 | 26 | 2 | kW | Float32
Connector 1 • Power factor | Input Register | 4 | 28 | 2 |  | Float32
Connector 1 • Total imported active energy in running session | Input Register | 4 | 30 | 2 | kWh | Float32
Connector 1 • Running session duration | Input Register | 4 | 32 | 4 | s | Int64
Connector 1 • Running session departure time | Input Register | 4 | 36 | 4 | s | Int64 | Unix time (seconds since 1970-01-01 00:00:00 UTC)
Connector 1 • Running session ID | Input Register | 4 | 40 | 4 |  | Int64 | In the case that charger is communicating with central system, this is a transactionId provided by central system over OCPP
Connector 1 • EV max power | Input Register | 4 | 44 | 2 | kW | Float32 | Max power detected in the currently running charging session
Connector 1 • EV planned energy | Input Register | 4 | 46 | 2 | kWh | Float32 | Total amount of energy that is planned to be delivered for currently running charging session
Connector 2 • Connnector status | Input Register | 4 | 100 | 1 |  | Int16 | ConnectorStatus
Connector 2 • Measured vehicle number of phases | Input Register | 4 | 101 | 1 |  | Int16 | NumberOfPhases
Connector 2 • EV max phase current | Input Register | 4 | 102 | 2 | A | Float32
Connector 2 • Target current from power mgm or modbus | Input Register | 4 | 104 | 2 | A | Float32
Connector 2 • Frequency | Input Register | 4 | 106 | 2 | Hz | Float32
Connector 2 • L-N voltage (L1) | Input Register | 4 | 108 | 2 | V | Float32
Connector 2 • L-N voltage (L2) | Input Register | 4 | 110 | 2 | V | Float32
Connector 2 • L-N voltage (L3) | Input Register | 4 | 112 | 2 | V | Float32
Connector 2 • Curent (L1) | Input Register | 4 | 114 | 2 | A | Float32
Connector 2 • Curent (L2) | Input Register | 4 | 116 | 2 | A | Float32
Connector 2 • Curent (L3) | Input Register | 4 | 118 | 2 | A | Float32
Connector 2 • Active power (L1) | Input Register | 4 | 120 | 2 | kW | Float32
Connector 2 • Active power (L2) | Input Register | 4 | 122 | 2 | kW | Float32
Connector 2 • Active power (L3) | Input Register | 4 | 124 | 2 | kW | Float32
Connector 2 • Active power (total) | Input Register | 4 | 126 | 2 | kW | Float32
Connector 2 • Power factor | Input Register | 4 | 128 | 2 |  | Float32
Connector 2 • Total imported active energy in running session | Input Register | 4 | 130 | 2 | kWh | Float32
Connector 2 • Running session duration | Input Register | 4 | 132 | 4 | s | Int64
Connector 2 • Running session departure time | Input Register | 4 | 136 | 4 | s | Int64 | Unix time (seconds since 1970-01-01 00:00:00 UTC)
Connector 2 • Running session ID | Input Register | 4 | 140 | 4 |  | Int64 | In the case that charger is communicating with central system, this is a transactionId provided by central system over OCPP
Connector 2 • EV max power | Input Register | 4 | 144 | 2 | kW | Float32 | Max power detected in the currently running charging session
Connector 2 • EV planned energy | Input Register | 4 | 146 | 2 | kWh | Float32 | Total amount of energy that is planned to be delivered for currently running charging session
Charger Settings
Charger • Serial number | Input Register | 4 | 990 | 10 |  | ASCII
Charger • Model | Input Register | 4 | 1000 | 10 |  | ASCII
Charger • HW version | Input Register | 4 | 1010 | 5 |  | ASCII
Charger • SW version | Input Register | 4 | 1015 | 5 |  | ASCII
Charger • Number of connectors | Input Register | 4 | 1020 | 2 |  | Int32
Connector 1 • Connector type | Input Register | 4 | 1022 | 1 |  | Int16 | ConnectorType
Connector 1 • Number phases | Input Register | 4 | 1023 | 1 |  | Int16 | NumberOfPhases
Connector 1 • L1 connected to phase | Input Register | 4 | 1024 | 1 |  | Int16 | Phase
Connector 1 • L2 connected to phase | Input Register | 4 | 1025 | 1 |  | Int16 | Phase
Connector 1 • L3 connected to phase | Input Register | 4 | 1026 | 1 |  | Int16 | Phase
Connector 1 • Custom max current | Input Register | 4 | 1028 | 2 | A | Float32
Connector 2 • Connector type | Input Register | 4 | 1122 | 1 |  | Int16 | ConnectorType
Connector 2 • Number phases | Input Register | 4 | 1123 | 1 |  | Int16 | NumberOfPhases
Connector 2 • L1 connected to phase | Input Register | 4 | 1124 | 1 |  | Int16 | Phase
Connector 2 • L2 connected to phase | Input Register | 4 | 1125 | 1 |  | Int16 | Phase
Connector 2 • L3 connected to phase | Input Register | 4 | 1126 | 1 |  | Int16 | Phase
Connector 2 • Custom max current | Input Register | 4 | 1128 | 2 | A | Float32
Power management modbus (socket 0.0.0.0:503)
Cluster Data
Building Load Guard • Connected | Input Register | 4 | 2000 | 1 |  | Bool
Building Load Guard • Frequency | Input Register | 4 | 2002 | 2 | Hz | Float32
Building Load Guard • L-N voltage phase (L1) | Input Register | 4 | 2004 | 2 | V | Float32
Building Load Guard • L-N voltage phase (L2) | Input Register | 4 | 2006 | 2 | V | Float32
Building Load Guard • L-N voltage phase (L3) | Input Register | 4 | 2008 | 2 | V | Float32
Building Load Guard • Curent (L1) | Input Register | 4 | 2010 | 2 | A | Float32
Building Load Guard • Curent (L2) | Input Register | 4 | 2012 | 2 | A | Float32
Building Load Guard • Curent (L3) | Input Register | 4 | 2014 | 2 | A | Float32
Building Load Guard • Active power (L1) | Input Register | 4 | 2016 | 2 | kW | Float32
Building Load Guard • Active power (L2) | Input Register | 4 | 2018 | 2 | kW | Float32
Building Load Guard • Active power (L3) | Input Register | 4 | 2020 | 2 | kW | Float32
Building Load Guard • Total active power | Input Register | 4 | 2022 | 2 | kW | Float32
Building Load Guard • Power factor | Input Register | 4 | 2024 | 2 |  | Float32
Power cluster • Curent (L1) | Input Register | 4 | 2100 | 2 | A | Float32
Power cluster • Curent (L2) | Input Register | 4 | 2102 | 2 | A | Float32
Power cluster • Curent (L3) | Input Register | 4 | 2104 | 2 | A | Float32
Power cluster • Active power (L1) | Input Register | 4 | 2106 | 2 | kW | Float32
Power cluster • Active power (L2) | Input Register | 4 | 2108 | 2 | kW | Float32
Power cluster • Active power (L3) | Input Register | 4 | 2110 | 2 | kW | Float32
Power cluster • Active power (total) | Input Register | 4 | 2112 | 2 | kW | Float32
Cluster Settings
Building LoadGuard • Installed | Input Register | 4 | 3000 | 1 |  | Bool

## Write registers
Write registers (Function code $16)
All values are written in big endian byte order in Modbus messages
Register addresses are not Modbus register names but the actual address values that must be written in messages
Parameter | Register Type | F. Code | Address | Words | Unit | Type | Enumeration or other details
Charger modbus (socket 0.0.0.0:502)
Connectors Commands
Connector 1 • Stop charging | Holding Register | 16 | 1 | 1 |  |  | Value ignored, triggered by write
Connector 1 • Pause charging | Holding Register | 16 | 2 | 1 |  |  | Value ignored, triggered by write
Connector 1 • Set departure time | Holding Register | 16 | 4 | 4 | s | Int64 | Unix time (seconds since 1970-01-01 00:00:00 UTC)
Connector 1 • Set current setpoint | Holding Register | 16 | 8 | 2 | A | Float32
Connector 1 • Cancel current setpoint | Holding Register | 16 | 10 | 1 |  |  | Value ignored, triggered by write
Connector 1 • Set power setpoint | Holding Register | 16 | 11 | 2 | kW | Float32
Connector 1 • Cancel power setpoint | Holding Register | 16 | 13 | 1 |  |  | Value ignored, triggered by write
Connector 2 • Stop charging | Holding Register | 16 | 101 | 1 |  |  | Value ignored, triggered by write
Connector 2 • Pause charging | Holding Register | 16 | 102 | 1 |  |  | Value ignored, triggered by write
Connector 2 • Set departure time | Holding Register | 16 | 104 | 4 | s | Int64 | Unix time (seconds since 1970-01-01 00:00:00 UTC)
Connector 2 • Set current setpoint | Holding Register | 16 | 108 | 2 | A | Float32
Connector 2 • Cancel current setpoint | Holding Register | 16 | 110 | 1 |  |  | Value ignored, triggered by write
Connector 2 • Set power setpoint | Holding Register | 16 | 111 | 2 | kW | Float32
Connector 2 • Cancel power setpoint | Holding Register | 16 | 113 | 1 |  |  | Value ignored, triggered by write
Charger commands
Charger • Set time | Holding Register | 16 | 1000 | 4 | s | Int64 | Unix time (seconds since 1970-01-01 00:00:00 UTC)
Charger • Restart | Holding Register | 16 | 1004 | 1 |  |  | Value ignored, triggered by write
Power management modbus (socket 0.0.0.0:503)
Cluster commands
Cluster • Set limit (L1) | Holding Register | 16 | 2000 | 2 | A | Float32
Cluster • Set limit (L2) | Holding Register | 16 | 2002 | 2 | A | Float32
Cluster • Set limit (L3) | Holding Register | 16 | 2004 | 2 | A | Float32
Custom write exceptions |  | http://www.simplymodbus.ca/exceptions.htm
Current setpoint too high |  | 12

## Enumerations
ConnectorStatus | ConnectorType | NumberOfPhases | Phase | PowerClusterMasterRole | Boolean
0 : Unknown | 1 : SocketType2 | 1 : Single phase | 1 : L1 | 1 : ActiveMaster | 0 : False
1 : SocketAvailable | 2 : PlugType2 | 2 : Two phase | 2 : L2 | 2 : StandbyMaster | 1 : True
2 : WaitingForVehicleToBeConnected |  | 3 : Three phase | 3 : L3
3 : WaitingForVehicleToStart
4 : Charging |  | 0: Three phases
5 : ChargingPausedByEv |  | 1 : Single phase (L1)
6 : ChargingPausedByEvse |  | 2 : Single phase (L2)
7 : ChargingEnded |  | 3 : Single phase (L3)
8 : ChargingFault |  | 4 : Unknown
9 : UnpausingCharging |  | 5 : Two phases
10 : Unavailable